## Tabelle1
				Hörschwelle nach DIN 45630-2

				Hörschwellenpegel in Abhängigkeit von der Terzmittenfrequenz / Terzmittenfrequenz in Hz / dB SPL

		Frequenz	dB HS
		8	103
		10	95
		12,5	87
		16	79
		20	71
		25	63
		31,5	55,5
		40	48
		50	40,5
		63	33,5
		80	28
		100	23,5

				Bild 1					Bild 2

Abschnitt 1
		Messung am Generator mit A Filter Bewertung

				File		A281_SPL_RTA

				SPL_RTA_full_band
				Timer mode		single
				Timer set		00:00:15
				Time weight		fast
				Selected filter		A-Weighting acc. IEC 61672
				Range		20 dB - 100 dB
				Mic sensitivity		19.57 mV/Pa

				ActTimer	LEQ[dB]	SPL_Act	MIN	MAX	LcPeak	OVER	OVER_Hold	UNDER
				00:00:00	63,2	63,4	62,6	63,9	82,4	0	0	0

		Messung am Generator mit C Filter Bewertung

				File		A282_SPL_RTA

				SPL_RTA_full_band
				Timer mode		single
				Timer set		00:00:15
				Time weight		fast
				Selected filter		C-Weighting acc. IEC 61672
				Range		20 dB - 100 dB
				Mic sensitivity		19.57 mV/Pa

				ActTimer	LEQ[dB]	SPL_Act	MIN	MAX	LcPeak	OVER	OVER_Hold	UNDER
				00:00:00	70,3	70,4	69,8	70,7	81,9	0	0	0

		Messung am Generator Terzmessung

				File		A283_SPL_RTA

				SPL_RTA_third_octave
				Timer mode		single					Spektrogramm 1
				Timer set		00:00:15
				Timer act		00:00:07
				RTA filter		Flat
				Time weight		fast
				Range		20 dB - 100 dB
				Mic sensitivity		19.57 mV/Pa

				Band[Hz]		LEQ[dB]	SPL[dB]	MIN[dB]	MAX[dB]		Blau = Hörschwelle (L HS)

				full_C-WTD	L HS	70,5	70,2	69,7	71,8		Frequenz in Hz / L EQ dB

				20	71	44,8	44,2	37,6	51,3
				25	63	43,7	40,8	35,9	52,6
				31,5	55,5	69,3	69,2	68,4	69,9
				40	48	56,3	52,7	42,3	66,7
				50	40,5	52,8	51,5	34,3	59,9
				63	33,5	58,2	58,1	57	59,5
				80	28	40,8	40,4	35,9	45,5
				100	23,5	56,7	57,5	54,7	58,3
				125		55,3	54,6	53,4	57,4
				160		61,6	61,7	60,3	62,8
				200		56,6	57,1	55	57,4
				250		59,2	59,2	57,5	60,9
				315		56,3	56,6	54	58,2
				400		56	55,6	53,6	57,5
				500		48,6	49,4	47,1	50
				630		52,3	53,2	50	54,4
				800		49,3	49,6	47,3	51,2
				1000		52,5	53	51,2	53,9
				1250		54,4	54,5	53,2	55,8
				1600		54,6	55,2	52,7	56,4
				2000		49,3	49,4	47,9	50,5				Bild 3
				2500		51	51,2	49,9	51,9
				3150		47,8	48,2	46,8	48,8
				4000		46,2	46	45,4	47,3
				5000		49,5	49,9	48,8	50,3
				6300		46,6	46,1	46	47,5
				8000		43,1	42,5	42,1	44,1
				10000		39,2	39,3	38,4	39,9
				12500		41,3	41,3	40,5	42,3
				16000		39,6	39,5	38,8	40,2
				20000		32,9	32,5	32,1	33,5

		Messung am Generator
				Frequenz in Hz / dB L
				File		A284_FFT

				FFT
				Mic sensitivity		19.57 mV/Pa

				f[Hz]	SPL[dB]
				10	54,7
				15,86	55,2
				21,72	52,7
				27,58	67,2
				33,44	69,4
				39,3	59,1
				45,16	41
				51,02	37,3
				56,88	45,4
				62,73	56,9
				68,59	55,4
				74,45	39,6
				80,31	36,3
				86,17	33,8
				92,03	49,7
				97,89	56,4				Bild 4
				103,75	51,2
				109,61	35,8
				115,47	39,8
				121,33	37,1
				127,19	48,6
				133,05	51,4
				138,91	43,3
				144,77	39,8
				150,62	42
				156,48	49
				162,34	61,3
				168,2	60,7
				174,06	46,7
				179,92	41,6
				185,78	39
				191,64	47,1
				197,5	55,4
				203,36	51,8
				209,22	33,6
				215,08	32,4
				220,94	36,3
				226,8	50,5
				232,66	54,5
				238,52	46
				244,38	37,6
				250,23	42,9
				256,09	45,8
				261,95	54,7
				267,81	55,4
				273,67	45
				279,53	45,3
				285,39	46,5
				291,25	46,1
				297,11	49,4					Bild 5
				302,97	47,3
				308,83	39,6
				314,69	42
				320,55	44
				326,41	44,6
				332,27	49,8
				338,12	46,5
				343,98	48
				349,84	43,5
				355,7	45,5
				361,56	48,5
				367,42	48,3
				373,28	42,4
				379,14	41,2
				385	42,1
				390,86	45,3
				396,72	51,9
				402,58	49,4
				408,44	42,2
				414,3	41,2
				420,16	38,5
				426,02	43,9
				431,88	46
				437,73	39
				443,59	38,6
				449,45	41,9
				455,31	42,3
				461,17	45,3
				467,03	45,3
				472,89	39
				478,75	37,5
				484,61	33,1
				490,47	28,8
				496,33	33					Bild 6
				502,19	34,7
				508,05	35,5
				513,91	34,1
				519,77	33,4
				525,62	39,1
				531,48	46,1
				537,34	42,5
				543,2	35,2
				549,06	36

		Messung am Generator					Orange = Hörschwelle (L HS)
				Frequenz in Hz / dB L
				File		A286_FFT

				FFT
				Mic sensitivity		19.57 mV/Pa

				f[Hz]	SPL[dB]	dB HS
				10	50,2	95
				12,93	50,7	87
				15,86	47,6	79
				18,79	44,7	71
				21,72	43,7
				24,65	38,8	63
				27,58	42,5
				30,51	65,2	55,5
				33,44	70,3
				36,37	63,7
				39,3	34,9	48
				42,23	30,7
				45,16	31,4
				48,09	37,8
				51,02	36,2	40,5
				53,95	37,4					Bild 7
				56,88	41,2
				59,8	44,6
				62,73	51,9	33,5			Messungen am Generator
				65,66	58,8				Der Honda Generator läuft während der Messung im Standby und ist daher noch relativ leise.
				68,59	55,8				Dieser Generator ist wahrscheinlich einer der leisesten am Markt. Ich persönlich empfinde diesen
				71,52	38,4				Generator als deutlich lauter und unangenehmer, als die meisten Wärmepumpen, die ich kenne.
				74,45	36,7
				77,38	36,5
				80,31	27,4	28
				83,24	31,9
				86,17	33,4
				89,1	35,1
				92,03	36,7
				94,96	36,4
				97,89	54,8
				100,82	57,6	23,5
				103,75	48,1
				106,68	38,5
				109,61	39
				112,54	36
				115,47	38,6
				118,4	35,3
				121,33	36,4
				124,26	41,8
				127,19	41,7
				130,12	46,4
				133,05	51,8
				135,98	48,5
				138,91	39,1
				141,84	33,1
				144,77	37,9
				147,7	39,6
				150,62	40,9
				153,55	38,7
				156,48	37,5
				159,41	40,1
				162,34	46,3
				165,27	61,2
				168,2	62
				171,13	50,5
				174,06	41,4
				176,99	39,3
				179,92	35,5
				182,85	31,5
				185,78	38,3
				188,71	40,2
				191,64	33,7
				194,57	36,3
				197,5	51
				200,43	57
				203,36	51,1
				206,29	31,8
				209,22	29,9
				212,15	29,1
				215,08	33,3
				218,01	32,8
				220,94	32,1
				223,87	31,6
				226,8	36,8
				229,73	43
				232,66	54,8
				235,59	53,3
				238,52	40
				241,45	37,5
				244,38	36,2
				247,3	32,1
				250,23	35,9
				253,16	36,6
				256,09	37,7
				259,02	40,3
				261,95	44,6
				264,88	54
				267,81	57,3
				270,74	49,4
				273,67	41,4
				276,6	42
				279,53	39,8
Abschnitt 2
				Orange= Hörschwelle (L HS)
	Schlafzimmer Fenster zu
				Frequenz in Hz / dB L
			File		A287_FFT

			FFT
			Mic sensitivity		19.57 mV/Pa

				f[Hz]	SPL[dB]	dB HS
				10	45,8	95
				12,93	37,1	87
				15,86	42,2	79
				18,79	37,2	71
				21,72	31,3
				24,65	31,3	63
				27,58	28
				30,51	46,5	55,5
				33,44	52,2
				36,37	46,5
				39,3	33,1	48
				42,23	27,1
				45,16	25,2
				48,09	31,5
				51,02	34,3	40,5
				53,95	27,2					Bild 8
				56,88	24,9
				59,8	21,5
				62,73	25,6	33,5
				65,66	34,4
				68,59	32,6
				71,52	20,1
				74,45	21,4
				77,38	18,4
				80,31	11,5	28
				83,24	14,1
				86,17	20,3
				89,1	21
				92,03	19,1
				94,96	14,9
				97,89	20,7
				100,82	24	23,5
				103,75	19,4
				106,68	19,5
				109,61	20,9
				112,54	19,4
				115,47	21,1
				118,4	14,4
				121,33	14,2
				124,26	9,3
				127,19	4,7
				130,12	16,4
				133,05	21,6
				135,98	18,8
				138,91	12
				141,84	7,8
				144,77	12,8
				147,7	15,6
				150,62	13,2
				153,55	14,8
				156,48	15					Spektrogramm 2
				159,41	14,4
				162,34	13,9
				165,27	25,4
				168,2	27,2
				171,13	17,1
				174,06	13,3
				176,99	16
				179,92	16,9
				182,85	14,5
				185,78	16,3
				188,71	19
				191,64	15,5
				194,57	15,2
				197,5	14,1
				200,43	21,8
				203,36	18,4
				206,29	10,2
				209,22	10,5
				212,15	5,5
				215,08	7
				218,01	13,7
				220,94	8,8
				223,87	8
				226,8	9,7
				229,73	16,2
				232,66	26
				235,59	26,8
				238,52	19,3
				241,45	14,8
				244,38	11,9
				247,3	6,4
				250,23	5,1
				253,16	5,8
				256,09	8
				259,02	9,4
				261,95	9
				264,88	5,8
				267,81	5
				270,74	5,7
				273,67	3,1
				276,6	3,2
				279,53	7,6

		Schlafzimmer Fenster zu

				File		A288_SPL_RTA

				SPL_RTA_full_band
				Timer mode		single
				Timer set		00:00:15
				Time weight		fast
				Selected filter		A-Weighting acc. IEC 61672
				Range		20 dB - 100 dB
				Mic sensitivity		19.57 mV/Pa

				ActTimer	LEQ[dB]	SPL_Act	MIN	MAX	LcPeak	OVER	OVER_Hold	UNDER
				00:00:00	31,7	31,5	31,3	35,8	61,1	0	0	1

		Schlafzimmer Fenster zu

				File		A289_SPL_RTA
				L CF – L AF > 20 dB		49,2 – 31,7 = 17,5
				SPL_RTA_full_band
				Timer mode		single
				Timer set		00:00:15
				Time weight		fast
				Selected filter		C-Weighting acc. IEC 61672
				Range		20 dB - 100 dB
				Mic sensitivity		19.57 mV/Pa

				ActTimer	LEQ[dB]	SPL_Act	MIN	MAX	LcPeak	OVER	OVER_Hold	UNDER
				00:00:00	49,2	51,9	47,5	51,1	57,8	0	0	0

Abschnitt 3

		Schlafzimmer Fenster auf

				File		A290_SPL_RTA

				SPL_RTA_full_band
				Timer mode		single
				Timer set		00:00:15
				Time weight		fast
				Selected filter		C-Weighting acc. IEC 61672
				Range		20 dB - 100 dB
				Mic sensitivity		19.57 mV/Pa

				ActTimer	LEQ[dB]	SPL_Act	MIN	MAX	LcPeak	OVER	OVER_Hold	UNDER
				00:00:00	64,3	64,7	63,6	66,4	77,3	0	0	0

		Schlafzimmer Fenster auf

				File		A292_SPL_RTA			L CF – L AF > 20 dB		64,3 -57,4 = 6,6

				SPL_RTA_full_band
				Timer mode		single
				Timer set		00:00:15
				Time weight		fast
				Selected filter		A-Weighting acc. IEC 61672
				Range		20 dB - 100 dB
				Mic sensitivity		19.57 mV/Pa

				ActTimer	LEQ[dB]	SPL_Act	MIN	MAX	LcPeak	OVER	OVER_Hold	UNDER
				00:00:00	57,4	57,4	56,9	57,8	75,7	0	0	0

		Schlafzimmer Fenster auf

				File		A294_SPL_RTA

				SPL_RTA_third_octave
				Timer mode		single
				Timer set		00:00:15
				Timer act		00:00:00
				RTA filter		C-Weighting acc. IEC 61672
				Time weight		fast
				Range		20 dB - 100 dB
				Mic sensitivity		19.57 mV/Pa
				Blau = Hörschwelle (L HS)
				Band[Hz]		LEQ[dB]	SPL[dB]	MIN[dB]	MAX[dB]
				Bild
				full_C-WTD	L HS	63,6	63,4	63	65	Frequenz in Hz / dB L

				20	71	38,1	42,1	24,4	47,1
				25	63	38,8	40,1	29,3	47,1
				31,5	55,5	58,5	57,2	57,1	59,7
				40	48	41,4	40,7	33,4	47,9
				50	40,5	41,7	34,7	31,6	49,9
				63	33,5	55,5	55,6	54,5	56,4
				80	28	36,5	35,6	32	41,2
				100	23,5	44,8	44,8	41,9	47,3
				125		44,2	44,9	40,6	46,4
				160		55,6	55,6	54,4	56,8
				200		55	54,8	53,9	55,9
				250		46,1	44,8	44,5	47,7
				315		37	37	34,9	39,3
				400		38,4	38,1	35,3	41,1
				500		37,8	37,7	35,6	39,5
				630		42,6	41,4	40,8	45,9
				800		43,6	44	41,2	45,6
				1000		46,2	46,4	44,5	47,6
				1250		42,8	43,9	41,4	44,2
				1600		46,4	47,6	44,3	48,3
				2000		47,1	46,1	45,6	48,5				Bild 9
				2500		42,5	42,1	41	43,8
				3150		43,1	42,4	42,1	44,1
				4000		43,7	42,2	42,5	44,8
				5000		47,8	46,1	46,7	48,8
				6300		44	43,1	43,2	44,9
				8000		39,5	39,5	38,3	40,7
				10000		34,7	33,5	34	35,5
				12500		31,8	30,8	30,8	32,7
				16000		25,2	24,1	24,2	26,1
				20000		17,6	17,5	17,5	17,7

				Orange = Hörschwelle (L HS)
		Schlafzimmer Fenster auf
				Frequenz in Hz / dB L
				File		A295_FFT

				FFT
				Mic sensitivity		19.57 mV/Pa

				f[Hz]	SPL[dB]	dB HS
				10	48,7	95
				12,93	45,3	87
				15,86	40,5	79
				18,79	45,1	71
				21,72	43,6
				24,65	37,8	63
				27,58	37,1
				30,51	57,1	55,5
				33,44	61,9
				36,37	55,1
				39,3	37	48
				42,23	35,3
				45,16	33,3
				48,09	29,1
				51,02	27,8	40,5
				53,95	25,7					Bild 10
				56,88	24,2
				59,8	31,1
				62,73	45	33,5
				65,66	55,4
				68,59	53,2
				71,52	35,9
				74,45	30,9
				77,38	25,7
				80,31	29,1	28
				83,24	29,8				Im gelben Fenster findet sich der Stein des Anstoßes:
				86,17	26,1				Bei geöffneten Fenster wurde ein Schalldruckpegel von 57,4 dB A gemessen.
				89,1	27,3				Viel zuviel Lärm, denn man sich nicht gefallen lassen muss.
				92,03	27,4				Also habe ich meinen eigenen Generator schnell wieder ausgeschaltet...
				94,96	29,9
				97,89	42,5
				100,82	45	23,5
				103,75	35,7
				106,68	29,3
				109,61	34,1
				112,54	33
				115,47	25,3
				118,4	23,6
				121,33	28,4
				124,26	28,6
				127,19	27,7
				130,12	39
				133,05	44
				135,98	38,1
				138,91	26
				141,84	28,2
				144,77	29,5
				147,7	33,5
				150,62	29,6
				153,55	25,9
				156,48	28,8
				159,41	31,7
				162,34	45
				165,27	55
				168,2	53,7
				171,13	38,4
				174,06	32,9
				176,99	29,6
				179,92	25,2
				182,85	28
				185,78	27,9
				188,71	28,1
				191,64	25,9
				194,57	36,2
				197,5	51,7
				200,43	54,4
				203,36	45
				206,29	28
				209,22	22,1
				212,15	18,2
				215,08	14,2
				218,01	19,7
				220,94	25,1
				223,87	20,7
				226,8	16,9
				229,73	35,7
				232,66	42,4
				235,59	37,8
				238,52	30,1
				241,45	25,3
				244,38	29,2
				247,3	28
				250,23	22
				253,16	23,9
				256,09	23,6
				259,02	22
				261,95	29,9
				264,88	40,5
				267,81	40,1
				270,74	29,6
				273,67	24,1
				276,6	21,1
				279,53	20,5
Abschnitt 4
		Schlafzimmer Fenster zu und Ruhe

				File		A296_SPL_RTA

				SPL_RTA_full_band
				Timer mode		single
				Timer set		00:00:15
				Time weight		fast
				Selected filter		A-Weighting acc. IEC 61672
				Range		20 dB - 100 dB
				Mic sensitivity		19.57 mV/Pa

				ActTimer	LEQ[dB]	SPL_Act	MIN	MAX	LcPeak	OVER	OVER_Hold	UNDER
				00:00:02	31,1	31,1	30,8	34,6	57,1	0	0	1

		Schlafzimmer Fenster zu und Ruhe

				File		A297_SPL_RTA

				SPL_RTA_full_band
				Timer mode		single
				Timer set		00:00:15
				Time weight		fast
				Selected filter		C-Weighting acc. IEC 61672
				Range		20 dB - 100 dB
				Mic sensitivity		19.57 mV/Pa

				ActTimer	LEQ[dB]	SPL_Act	MIN	MAX	LcPeak	OVER	OVER_Hold	UNDER
				00:00:00	39,9	36,1	35,1	46,9	53,9	0	0	0

		Schlafzimmer Fenster zu und Ruhe					Orange = Hörschwelle (L HS)

				Frequenz in Hz / dB L
				File		A299_FFT

				FFT
				Mic sensitivity		19.57 mV/Pa

				f[Hz]	SPL[dB]	dB HS
				10	42,6	95
				12,93	37,3	87
				15,86	34,6	79
				18,79	35	71
				21,72	34,4
				24,65	31,6	63
				27,58	31,2
				30,51	34,6	55,5
				33,44	38,6
				36,37	33,3
				39,3	19,6	48
				42,23	21,6
				45,16	26,8
				48,09	29,3
				51,02	25,1	40,5
				53,95	21,4
				56,88	24,2
				59,8	25
				62,73	20,9	33,5
				65,66	19,6					Bild 11
				68,59	18,7
				71,52	15,4
				74,45	16,6
				77,38	14,8
				80,31	13,5	28
				83,24	13,4
				86,17	17,2
				89,1	17,1
				92,03	16,6
				94,96	16,5
				97,89	17,9
				100,82	16,4	23,5
				103,75	14,1
				106,68	15
				109,61	13,6
				112,54	14,4
				115,47	10
				118,4	14
				121,33	17,9
				124,26	9,8
				127,19	10,3
				130,12	16,4
				133,05	16,8
				135,98	11,4
				138,91	7,4
				141,84	16,9
				144,77	16,5
				147,7	15,7
				150,62	19,3
				153,55	17,1
				156,48	12,4					Spektrogramm 3
				159,41	12,9
				162,34	16,7
				165,27	11,7
				168,2	9,9
				171,13	10,5
				174,06	13,4
				176,99	12,2
				179,92	10,4
				182,85	11,2
				185,78	12,9
				188,71	13
				191,64	11,4
				194,57	12,3
				197,5	8,9
				200,43	11,1
				203,36	6,1
				206,29	8,7
				209,22	8,6
				212,15	10,2
				215,08	10,8
				218,01	8,5
				220,94	12,1
				223,87	10,6
				226,8	7,1					Bild 13
				229,73	6
				232,66	3,6
				235,59	9,6
				238,52	11,4
				241,45	12,5
				244,38	5,8
				247,3	7,1				Hier sind typische Pegelwerte bei „Stille auf dem Land zu sehen“.
				250,23	6,2				Wie man deutlich erkennt, ist auch bei Stille grundsätzlich tieffrequenter
				253,16	6,3				Schall zu messen. Auf unserer Erde gibt es keine absolute Stille!
				256,09	12,3				Auch wenn wir nichts hören, kann man immer Schall messen.
				259,02	9,9
				261,95	3,8
				264,88	10,2
				267,81	12
				270,74	8
				273,67	9,3
				276,6	8,2
				279,53	5,4